## Piping Material Specification
[5 empty] | PIPING MATERIAL SPECIFICATION | [12 empty] | Rev: 0
[5 empty] | Piping Class |  |  |  | Material |  |  | C.A |  |  | Mill Tol |  |  | Sheet No.
[5 empty] | A1LN |  | 150# |  | LTCS NACE |  |  | 3 mm |  |  | 12.5% |  |  | 0
[5 empty] | Design Code: |  |  | ASME B 31.3, NACE-MR-01-75/ISO-15156-1/2/3
[5 empty] | Service: |  |  | Flare, Corrosive HC service (Low Temp)
[5 empty] | Branch Chart: |  |  | Ref. APPENDIX-1, Chart 1
Pressure-Temperature Rating
Press., barg | 19.6 |  | 19.2 |  | 17.7 |  | 15.8 |  | 13.8 | [5 empty] | Hydrotest Pr. (barg)
Temp., °C | -45 to 38 |  | 50 |  | 100 |  | 150 |  | 200 | [5 empty] | 29.4
Pipe Data
Code | ASME B 36.10M
Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30
O.D.mm | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4 | 457 | 508 | 559 | 610 | 660 | 711 | 762
Sch. | 160 | 160 | 160 | 160 | XS | XS | XS | XS | XS | XS | XS | XS | XS | XS | XS | XS | XS | XS | XS | XS
WT. mm | 4.78 | 5.56 | 6.35 | 7.14 | 5.54 | 7.62 | 8.56 | 10.97 | 12.7 | 12.7 | 12.7 | 12.7 | 12.7 | 12.7 | 12.7 | 12.7 | 12.7 | 12.7 | 12.7 | 12.7
TYPE | Seamless | [12 empty] | EFW, 100% RT
MOC | ASTM A 333 Gr.6 | [12 empty] | ASTM A 671 - CC60 Class 22
Ends | BE
Fittings Data
TYPE | Butt Weld (SCH to match pipe), Seamless | [12 empty] | Butt Weld (SCH to match pipe), Welded
MOC | ASTM A 420 Gr. WPL6
Elbow | ASME B 16.9
Tee | ASME B 16.9
Red. | ASME B 16.9
Cap | ASME B 16.9
Plug | Hex Head Plug, ASME B 16.11
Weldolet | MSS SP 97, ASTM A 350 Gr. LF2
Flange
MOC | ASTM A 350 Gr. LF2
FACE | 150# RF, Serrated Finish
TYPE | Weld Neck, ASME B 16.5/ 16.47A, Butt Welding ends as per ASME B 16.25
Spectacle Blind/Spacer Blinds
MOC | ASTM A 350 Gr. LF2
Spectacle | ASME B 16.48 | [10 empty] | Spacer and blind as per ASME B 16.48
Bolts/ Nuts/ Gaskets
Stud Bolts | ASTM A 320 Gr. L7M, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Hex Nuts | ASTM A 194 Gr. 7ML, XYLAR 2 + XYLAN 1070 coated with minimum combined thickness of 50μm
Gasket | ASME B 16.20, 4.5 mm, SS316/SS316L Spiral Wound with Flexible Graphite (F.G.) filler
Valves
Rating | 150#, RF
Ball | BLRTA1LNT |  |  |  | BLRTA1LNR
Gate | GAYMA1LNT |  |  |  | GAYMA1LNR
Globe | GLYMA1LNT |  |  |  | GLYMA1LNR
Check | CHPMA1LNT |  |  |  | CHPMA1LNR
Notes
1. PMS to be read in conjunction with Piping Design Basis, Doc No. PMS-001 and Valve Material Specification.
2. Weld Joint Factor for welded pipe shall be as per ASME B 31.3.
3. Welded fittings shall be 100% radiographed.
4. Two jackscrew, 180 degree apart shall be provided in one of the flanges for all orifice flange and specified spectacle blind assemblies.
5. Spectacle blinds and spacer sizes and rating that are not available in ASME B 16.48 shall be as per manuf. standard. Design shall be submitted to Company for review and approval.
6. Maximum temperature limit for all Soft Seat Ball Valve shall be 200°C.
7. Wafer check valve to be avoided, unless the available space constraint does not allow normal check valve.