## Piping Material Specification
PIPING MATERIAL SPECIFICATION
PMS Project ¦ PMS-001 ¦ Rev. 0
Spec Code: | A2 | Material: |  | Material: | A106 Gr.B (CS)
Design Pressure: | 150 psig | Design Temperature: |  | Design Temperature: | 300 degF (148.9 degC)
Test Pressure: | 225 psig | MDMT: |  | MDMT: | -20 degF
Corrosion Allowance: | 3 mm | Service/Fluid: |  | Service/Fluid: | Process Water
Pipe Schedule: | Sch 10S | Joint Type: |  | Joint Type: | seamless (E=1)
Item | Component | Description | Size Range | Material | Standard | Rating | Remarks
PIPES
1 | Pipe, Seamless | ASTM A106 Gr.B, BW, Sch 10S | NPS 0.5 - 24 | A106 Gr.B | ASME B36.10 | Sch 10S | WT: 6.35 mm
FITTINGS
2 | 90 deg LR Elbow | BW, Sch 10S | NPS 0.5 - 24 | A234 WPB | ASME B16.9 | Sch 10S
3 | 45 deg Elbow | BW, Sch 10S | NPS 0.5 - 24 | A234 WPB | ASME B16.9 | Sch 10S
4 | Equal Tee | BW, Sch 10S | NPS 0.5 - 24 | A234 WPB | ASME B16.9 | Sch 10S
5 | Reducing Tee | BW, Sch 10S | NPS 0.5 - 24 | A234 WPB | ASME B16.9 | Sch 10S
6 | Concentric Reducer | BW, Sch 10S | Per run/branch | A234 WPB | ASME B16.9 | Sch 10S
7 | Eccentric Reducer | BW, Sch 10S | Per run/branch | A234 WPB | ASME B16.9 | Sch 10S
8 | Pipe Cap | BW, Sch 10S | NPS 0.5 - 24 | A234 WPB | ASME B16.9 | Sch 10S
9 | Weldolet | Branch connection, BW | Per branch size | A234 WPB | MSS SP-97 | Sch 10S | 2+ size reduction
10 | Sockolet | Branch connection, SW | NPS 0.5 - 2 | A234 WPB | MSS SP-97 | 3000# | Small bore branches
FLANGES
11 | Weld Neck Flange | Raised Face | NPS 0.5 - 24 | A105 | ASME B16.5 | #150 | Face finish: 125-250 AARH
12 | Slip-On Flange | Raised Face | NPS 0.5 - 24 | A105 | ASME B16.5 | #150
13 | Blind Flange | Raised Face | NPS 0.5 - 24 | A105 | ASME B16.5 | #150
GASKETS
14 | Spiral Wound Gasket | CS/Graphite, Inner ring: CS, Filler: Graphite | NPS 0.5 - 24 | CS/Graphite | ASME B16.20 | #150
BOLTING
15 | Stud Bolt | Continuous thread, A193 B7 | Per flange | A193 B7 | ASME B16.5 |  | Temp range: -29 to 400 degC
16 | Hex Nut | Heavy series, A194 2H | Per flange | A194 2H | ASME B18.2.2
VALVES
17 | Gate Valve | Flanged RF, Body: A216 WCB | NPS 0.5 - 24 | A216 WCB | API 600 | #150 | Trim: 13Cr/Stellite, Seat: 13Cr, VDS: VDS-A2-GA-001
18 | Globe Valve | Flanged RF, Body: A216 WCB | NPS 0.5 - 24 | A216 WCB | BS 1873 | #150 | Trim: 13Cr/Stellite, Seat: 13Cr, VDS: VDS-A2-GL-002
19 | Check Valve | Flanged RF, Body: A216 WCB | NPS 0.5 - 24 | A216 WCB | BS 1868 | #150 | Trim: 13Cr, Seat: 13Cr, VDS: VDS-A2-CH-003
20 | Ball Valve | Flanged RF, Body: A216 WCB | NPS 0.5 - 24 | A216 WCB | API 6D | #150 | Trim: SS316, Seat: PTFE/RPTFE, VDS: VDS-A2-BA-004
21 | Butterfly Valve | Flanged RF, Body: A216 WCB | NPS 0.5 - 24 | A216 WCB | API 609 | #150 | Trim: SS316, Seat: EPDM/PTFE, VDS: VDS-A2-BU-005
NOTES
1. All dimensions per ASME/ANSI standards.
2. Pipe wall thickness calculated per ASME B31.3.
3. Min required thickness: 0.2375 in (6.03 mm) including CA and 12.5% mill tolerance.
4. Flange ratings per ASME B16.5 at 300 degF.
5. All butt weld fittings per ASME B16.9. Socket weld fittings per ASME B16.11.
6. Gaskets per ASME B16.20. Bolting per ASME B16.5.
7. Weld end preparation per ASME B16.25.
8. Line blanks (spectacle blinds) per ASME B16.48 where required.