## Piping Material Specification
[5 empty] | PIPING MATERIAL SPECIFICATION | [11 empty] | Rev: 0
[5 empty] | Piping Class |  |  | Material |  |  | C.A |  |  | Mill Tol |  | Sheet No.
[5 empty] | G4L |  | 150# | Carbon Steel |  |  | 1.5 mm |  |  | 0.125 |  | 0
[5 empty] | Design Code: |  |  | ASME B 31.3
[5 empty] | Service: |  | Process Water
[5 empty] | Branch Chart: |  |  | Per ASME B31.3 para 304.3
Pressure-Temperature Rating
Press., barg | 19.7 |  | 17.9 |  | 15.9 |  | 13.8 |  | 11.7 |  | 9.7 |  | Hydrotest Pr. (barg)
Temp., deg C | -29 to 38 |  | 93 |  | 149 |  | 204 |  | 260 |  | 316 |  | 15.5
Pipe Data
Code | ASME B 36.10M
Size (in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24 | 30 | 36
O.D. mm | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.8 | 355.6 | 406.4 | 457.2 | 508 | 609.6 | 762 | 914.4
Sch. | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S
WT. mm | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 2.11 | 2.11 | 2.77 | 2.77 | 3.4 | 3.96 | 3.96 | 4.19 | 4.19 | 4.78 | 5.54 | 6.35 | 7.92
TYPE | Seamless
MOC | ASTM A106 Gr.B
Ends | BE
Fittings Data
TYPE | Butt Weld (SCH to match pipe), Seamless
MOC | A234 WPB
Elbow | ASME B 16.9
Tee | ASME B 16.9
Red. | ASME B 16.9
Cap | ASME B 16.9
Plug | Hex Head Plug, ASME B 16.11
Weldolet | MSS SP 97, A234 WPB
Flange
MOC | A105
Rating | 150#, Raised Face
TYPE | Weld Neck, ASME B16.5, Butt welding ends as per ASME 16.25, Raised Face
Compact Flange | N/A - per project specification
Hub Connector | N/A - per project specification
Spectacle Blind/Spacer Blinds
MOC | A105
Spectacle | ASME B 16.48 | [10 empty] | Spacer and blind as per ASME B 16.48
Bolts/ Nuts/ Gaskets
Stud Bolts | A193 B7
Hex Nuts | A194 2H
Gasket | ASME B16.20, Spiral Wound of CS/Graphite, Inner: CS, Filler: Graphite
Valves
Rating | 150#, Raised Face
Ball | A216 WCB, VDS: BLRTG4LR
Gate | A216 WCB, VDS: GAYMG4LR
Globe | A216 WCB, VDS: GLYMG4LR
Check | A216 WCB, VDS: CHPMG4LR
Butterfly | A216 WCB, VDS: BFWTG4LR
Needle | A105, VDS: NEIPG4LR
DBB | A216 WCB, VDS: DBMPG4LR
Notes
1. PMS to be read in conjunction with project piping design basis. PMS-001
2. Weld Joint Factor for welded pipe shall be as per ASME B 31.3.
3. Min required wall thickness: 0.0959 in (2.43 mm) incl CA and 12.5% mill tolerance.
4. Flange ratings per ASME B16.5 at design temperature 300 degF.
5. All butt weld fittings per ASME B16.9. Socket weld fittings per ASME B16.11.
6. Gaskets per ASME B16.20. Bolting per ASME B16.5.
7. PWHT: Per Code. NDE: 10% RT.
8. Hydrotest medium: Water.
9. Branch reinforcement per ASME B31.3 para 304.3 where required.
10. MDMT: -20 degF - UCS-66 Curve B applies. Verify impact test exemption.