## Piping Material Specification
[5 empty] | PIPING MATERIAL SPECIFICATION | [11 empty] | Rev: 0
[5 empty] | Piping Class |  |  | Material |  |  | C.A |  |  | Mill Tol |  | Sheet No.
[5 empty] | T60C |  | 150# | Stainless Steel |  |  | 0 mm |  |  | 0.125 |  | 0
[5 empty] | Design Code: |  |  | ASME B 31.3
[5 empty] | Service: |  | Process Water
[5 empty] | Branch Chart: |  |  | Per ASME B31.3 para 304.3
Pressure-Temperature Rating
Press., barg | 19 |  | 16.5 |  | 14.8 |  | 13.4 |  | 12.1 |  | 11 |  | Hydrotest Pr. (barg)
Temp., deg C | -29 to 38 |  | 93 |  | 149 |  | 204 |  | 260 |  | 316 |  | 15.5
Pipe Data
Code | ASME B 36.19M
Size (in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24 | 30 | 36
O.D. mm | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.8 | 355.6 | 406.4 | 457.2 | 508 | 609.6 | - | -
Sch. | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | 5S | - | -
WT. mm | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 2.11 | 2.11 | 2.77 | 2.77 | 3.4 | 3.96 | 3.96 | 4.19 | 4.19 | 4.78 | 5.54 | - | -
TYPE | Seamless
MOC | ASTM B677 A312 TP316
Ends | BE
Fittings Data
TYPE | Butt Weld (SCH to match pipe), Seamless
MOC | A403 WP316
Elbow | ASME B 16.9
Tee | ASME B 16.9
Red. | ASME B 16.9
Cap | ASME B 16.9
Plug | Hex Head Plug, ASME B 16.11
Weldolet | MSS SP 97, A403 WP316
Flange
MOC | A182 F316
Rating | 150#, Raised Face
TYPE | Weld Neck, ASME B16.5, Butt welding ends as per ASME 16.25, Raised Face
Compact Flange | N/A - per project specification
Hub Connector | N/A - per project specification
Spectacle Blind/Spacer Blinds
MOC | A182 F316
Spectacle | ASME B 16.48 | [10 empty] | Spacer and blind as per ASME B 16.48
Bolts/ Nuts/ Gaskets
Stud Bolts | A193 B8
Hex Nuts | A194 8
Gasket | ASME B16.20, Spiral Wound of SS304/Graphite, Inner: SS304, Filler: Graphite/PTFE
Valves
Rating | 150#, Raised Face
Ball | A351 CF8M, VDS: BLRTT60CR
Gate | A351 CF8M, VDS: GAYMT60CR
Globe | A351 CF8M, VDS: GLYMT60CR
Check | A351 CF8M, VDS: CHPMT60CR
Butterfly | N/A
Needle | A182 F316, VDS: NEIPT60CR
DBB | A351 CF8M, VDS: DBMPT60CR
Notes
1. PMS to be read in conjunction with project piping design basis. PMS-001
2. Weld Joint Factor for welded pipe shall be as per ASME B 31.3.
3. Min required wall thickness: 0.0298 in (0.76 mm) incl CA and 12.5% mill tolerance.
4. Flange ratings per ASME B16.5 at design temperature 300 degF.
5. All butt weld fittings per ASME B16.9. Socket weld fittings per ASME B16.11.
6. Gaskets per ASME B16.20. Bolting per ASME B16.5.
7. PWHT: Per Code. NDE: 10% RT.
8. Hydrotest medium: Water.
9. Branch reinforcement per ASME B31.3 para 304.3 where required.
10. MDMT: -20 degF - Austenitic SS, impact test not required.