## PMS Sheet
PIPING MATERIAL SPECIFICATION (PMS)
Project | PMS Project
Document No | PMS-001
Revision | 0
Date | 2026-02-08
Spec Code | A2
1. GENERAL INFORMATION
Base Material | A106 Gr.B
Material Type | CS
Material Spec | ASTM A106
Corrosion Allowance | 3 mm
Service/Fluid | Process Water
Line Number | 6-P-1001-A1-1H
2. DESIGN CONDITIONS
Parameter | Value | Unit
Design Pressure | 150 | psig
Test Pressure | 225 | psig
Design Temperature | 300 | degF | 148.9 degC
MDMT | -20 | degF | -28.9 degC
Operating Pressure | 120 | psig
Operating Temperature | 240 | degF
Pipe Size | NPS 6
3. PIPE WALL THICKNESS & SCHEDULE
Code | ASME B31.3
Allowable Stress | 20000 psi
Joint Efficiency | 1 | seamless
Calc. Thickness | 0.0248 in
Min Req. Thickness (w/CA) | 0.1429 in
Schedule Standard | ASME B36.10
Selected Schedule | 40
Wall Thickness | 0.28 in | 7.11 mm
Pipe OD | 6.625 in
Pipe ID | 6.065 in
4. PIPE & FITTINGS
Component | Material | Standard | Schedule
Pipe | A106 Gr.B | ASTM | 40
90 deg LR Elbow | A234 WPB | ASME B16.9 | Sch 40 / STD
45 deg Elbow | A234 WPB | ASME B16.9 | Sch 40 / STD
Equal Tee | A234 WPB | ASME B16.9 | Sch 40 / STD
Reducing Tee | A234 WPB | ASME B16.9 | Sch 40 / STD
Concentric Reducer | A234 WPB | ASME B16.9 | Sch 40 / STD
Eccentric Reducer | A234 WPB | ASME B16.9 | Sch 40 / STD
Pipe Cap | A234 WPB | ASME B16.9 | Sch 40 / STD
5. FLANGES, GASKETS & BOLTING
FLANGE
Pressure Class | #150
Material | A105
Types | WN/SO/BL
Face Type | Raised Face (RF)
GASKET
Type | Spiral Wound
Material | CS/Graphite
Standard | ASME B16.20
BOLTING
Stud Bolt | A193 B7
Nut | A194 2H
Temp Range | -29 to 400 degC
6. VALVES
Type | Body Material | Trim | Seat | VDS Tag
Ball | A216 WCB | SS316 | PTFE/RPTFE | VDS-A2-BA-004
Butterfly | A216 WCB | SS316 | EPDM/PTFE | VDS-A2-BU-005
Check | A216 WCB | 13Cr | 13Cr | VDS-A2-CH-003
Gate | A216 WCB | 13Cr/Stellite | 13Cr | VDS-A2-GA-001
Globe | A216 WCB | 13Cr/Stellite | 13Cr | VDS-A2-GL-002