## Piping Material Specification
[5 empty] | PIPING MATERIAL SPECIFICATION | [12 empty] | Rev: 0
[5 empty] | Piping Class |  |  |  | Material |  |  | C.A |  |  | Mill Tol |  |  | Sheet No.
[5 empty] | A1 |  | 150# |  | Carbon Steel |  |  | 3 mm |  |  | 12.5% |  |  | 0
[5 empty] | Design Code: |  |  | ASME B 31.3
[5 empty] | Service: |  |  | Cooling Water, HM, Diesel, Steam, WI, HC with low CO2 and H2S, Fresh Water, Hydraulic, Nitrogen, Exhaust, Fuel Oil, Tank Air Vent
[5 empty] | Branch Chart: |  |  | Ref. APPENDIX-1, Chart 1
Pressure-Temperature Rating
Press., barg | 19.6 |  | 19.2 |  | 17.7 |  | 15.8 |  | 13.8 |  | 12.1 |  | 10.2 |  |  |  | Hydrotest Pr. (barg)
Temp., °C | -29 to 38 |  | 50 |  | 100 |  | 150 |  | 200 |  | 250 |  | 300 |  |  |  | 29.4
Pipe Data
Code | ASME B 36.10M
Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30
O.D.mm | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4 | 457 | 508 | 559 | 610 | 660 | 711 | 762
Sch. | XXS | XXS | XXS | XXS | 160 | 160 | 120 | 120 | 100 | 60 | 60 | 60 | 60 | 40 | 40 | 30 | 30 | XS | 30 | 30
WT. mm | 7.47 | 7.82 | 9.09 | 10.16 | 8.74 | 11.13 | 11.13 | 14.27 | 15.09 | 12.7 | 14.27 | 15.09 | 16.66 | 14.27 | 15.09 | 12.7 | 14.27 | 12.7 | 15.88 | 15.88
TYPE | Seamless | [12 empty] | EFW, 100% RT
MOC | ASTM A 106 Gr. B | [12 empty] | ASTM A 672 Gr. B60 Class 12
Ends | BE
Fittings Data
TYPE | Butt Weld (SCH to match pipe), Seamless | [12 empty] | Butt Weld (SCH to match pipe), Welded
MOC | ASTM A 234 Gr. WPB
Elbow | ASME B 16.9
Tee | ASME B 16.9
Red. | ASME B 16.9
Cap | ASME B 16.9
Plug | Hex Head Plug, ASME B 16.11 |  |  |  | -
Weldolet | MSS SP 97, ASTM A 105
Flange
MOC | ASTM A 105
FACE | 150# RF, Serrated Finish
TYPE | Weld Neck, ASME B 16.5/ 16.47A, Butt Welding ends as per ASME B 16.25
Spectacle Blind/Spacer Blinds
MOC | ASTM A 105
Spectacle | ASME B 16.48 | [10 empty] | Spacer and blind as per ASME B 16.48
Bolts/ Nuts/ Gaskets
Stud Bolts | ASTM A 193 Gr. B7
Hex Nuts | ASTM A 194 Gr. 2H
Gasket | ASME B 16.20, 4.5 mm, SS316/SS316L Spiral Wound with Flexible Graphite (F.G.) filler
Valves
Rating | 150#, RF
Ball | BLRTA1T |  |  |  | BLRTA1R
Gate | GAYMA1T |  |  |  | GAYMA1R
Globe | GLYMA1T |  |  |  | GLYMA1R
Check | CHPMA1T |  |  |  | CHPMA1R
Notes
1. PMS to be read in conjunction with Piping Design Basis, Doc No. PMS-001 and Valve Material Specification.
2. Weld Joint Factor for welded pipe shall be as per ASME B 31.3.
3. Welded fittings shall be 100% radiographed.
4. Two jackscrew, 180 degree apart shall be provided in one of the flanges for all orifice flange and specified spectacle blind assemblies.
5. Spectacle blinds and spacer sizes and rating that are not available in ASME B 16.48 shall be as per manuf. standard. Design shall be submitted to Company for review and approval.
6. Maximum temperature limit for all Soft Seat Ball Valve shall be 200°C.
7. Wafer check valve to be avoided, unless the available space constraint does not allow normal check valve.